## Sheet1
[6 empty] | Client |  | Reference
Item | Cable sizing calculation proceedure |  |  |  | Comments, hints | Project |  | Designer
| Enter phase voltage | V | = | 230
1 | Enter the design current for the load | In | = | 0 |  | Supply line voltage | VL
2 | Select the protective device size | Ib | = | 0 | 6, 10, 16, 20, 32 etc. | Design Current | In
| Ensure In > Ib |  |  |  | (Logical test cell is blank if Ib = 0) | Protective device size | Ib
3 | Enter correction factors | Ca | = | 1 | Ambient Temperature from table 4C1 and 4C2 (appendix 4) | Correction factors | Ca | 1 | Ambient
| Note: Use a factor of "1" where no factor applies to avoid the devide by zero error. | Cg | = | 1 | Grouping, from tables 4B1, 4B2 and 4B3 (ignore if spaced more than 2d apart or if loaded to less than 30%) |  | Cg | 1 | Grouping | Minimum cable size | 0
| Other correction factors like cable operating temperatures and thermal insulation are applied via cable selection methods in table 4A1 and 4D1A to 4L4B. | Cp | = | 1 | Putting aside BS3036 fuses as they are rarely used, add a Cp factor of 1.5 (0.67-1) for ring final circuits, otherwise a 2.5 mm2 cable would fail. |  | Cp | 1 | Device (1.5 for ring with MCB) | Minimum cable size, use largest of the two | 0
4 | Find the minimum cable size needed. | It | >= | 0 | In tables 4D1A to 4L4B.
|  | It | >= | 0 | Note: use which ever is the greater value of "It"
| Tabulated Voltage Drop | mV/A/m | = | 0 | From tables 4D1A to 4L4B.
| Maximum pemitted cable temp oC | tp | = | 0 | 70o for PVC, 90o for XLPE etc see tables 4D1A to 4L4B
| Correction for ambient temperature | Ct | = |  | Note: for temperatures above 30oC and cables 16mm2 or smaller only.
| length of run | l | = | 0
5 | Voltage Drop | Vd | = |  | Add the voltage drop on each cable length and determine the percentage of drop from supply to load.
| Note: for cables above 16mm2 use: | r | = | 0 | From tables 4D1A to 4L4B.
| r and x values to obtain a corrected z value | x | = | 0 | From tables 4D1A to 4L4B.
| Voltage Drop | Vd | = | 0 | Add the voltage drop on each cable length and determine the percentage of drop from supply to load.
| Enter the impedance external to this circuit. | Ze | = | 0 | The impedance of from the source to the panel or board supplying the cable.
| Enter impedance of cable Z1 | Z1 | = | 0 | One leg of the conductor only
6 | Enter impedance of CPC Z2 | Z2 | = | 0 | Effectively the return path
| Circuit Impedance | Zs | = | 0 | Check Zs against tables 41B1 to 41D
7 | Earth fault current | Ief | = |  | Required for disconnection time
| Disconnection time | t | = | 0 | Regulations 413-02-11 and 413-02-12 (230 volt 0.4s or 5s)
| k factor for insulation and conductor | k | = | 0 | Tables 54B, C, D, E and F
| Actual disconection time of protective device | t | = | 0 | under a fault of negligable impedance.
8 | Thermal constraint | S | = |  | = Minimum CSA of the CPC in mm2
9 | Duration of fault | t | = |  | If less than 0.1 sec then check K2S2 > I2t of the protective device